## Sheet 1 - product_recalls_downl
product_recalls_download-1704894864
Recall Number | Date | Recall Heading | Name of product | Description | Hazard Description | Remedy Type | Units | Incidents | Remedy | Sold At Label | Sold At | Importers | Manufacturers | Distributors | Manufactured In | Custom Label | Custom Field
21-130 | May 06, 2021 | Kidde Recalls TruSense Smoke and Combination Smoke/Carbon Monoxide Alarms Due to Risk of Failure to Alert Consumers to a Fire | Kidde TruSense Smoke Alarms and Combination Smoke/Carbon Monoxide Alarms | This recall involves Kidde TruSense Smoke Alarms and Combination Smoke/Carbon Monoxide Alarms. &nbsp;The recalled units are Kidde Model Series 2040, 2050, 2060 and 2070 Smoke and Combination Smoke/Carbon Monoxide alarms. &nbsp;Only alarms with the TruSense logo or “AMBER=FAULT” printed on the front of the alarm are included in this recall. &nbsp;The model number is printed on the back of the alarm. Model Alarm Type 2040-DSR Smoke 2050-DS10 Smoke 2060-ASR Smoke 2070-VDSCR Combination Smoke/Carbon Monoxide 2070-VASCR Combination Smoke/Carbon Monoxide 2070-VDSR Smoke 2070-VASR Smoke | The smoke alarm and the combination smoke/carbon monoxide (CO) alarm can fail to alert consumers to a fire. | Replace | About 226,000 | No incidents or injuries have been reported. | Consumers should immediately contact Kidde for a free replacement alarm. Consumers should keep using the recalled alarms until they install replacement alarms. | Sold At | Walmart, Home Depot, Menards and other department, home and hardware stores and electrical distributors nationwide, and online at Amazon.com, ShopKidde.com and other online retailers from May 2019 through September 2020 for between $10 and $70. | Walter Kidde Portable Equipment Company Inc., of Mebane, N.C. |  |  | China
21-085 | February 24, 2021 | Potter Electric Recalls Addressable Pull Stations Single/Dual Action Due to Failure to Alert to Fire | Potter Electric Addressable Pull Stations Single/Dual Action | This recall involves Potter Electric Addressable Pull Stations.&nbsp; When manually pulled, these red-colored devices are intended to activate a fire alarm in commercial and other buildings.&nbsp; Recalled models include: &nbsp;(1) Potter Electric Addressable Dual Action Pull Station, Model PAD100-PSDA, Part Number 3992720, with a date code Dec 03 2020; and (2)&nbsp;Potter Electric Addressable Single Action Pull Station, Model PAD100-PSSA, Part Number 3992721, with date codes Nov 10 2020, Nov 25 2020, Dec 01 2020, and Dec 03 2020.&nbsp; “Potter” is printed on the front of all devices.&nbsp; The date code is located inside the device. | The pull handle on some units can fail to activate the fire alarm system when manually pulled, posing a risk of failure to alert consumers to a fire. | Replace | About 735 | No incidents or injuries have been reported. | Consumers should immediately contact Potter Electric or their fire alarm system dealers/installers for a free replacement. All known Potter Electric distributors and dealers/installers have been notified directly by the firm. | Sold At | Authorized Potter dealers and distributors nationwide from December 2020 through January 2021 for between approximately $100 and $135. |  | Potter Electric Signal Company, LLC, of St. Louis, Mo. |  | U.S.
20-140 | June 17, 2020 | Edwards Recalls Mechanical Heat Detectors Due to Failure to Alert to Fire | Edwards Mechanical Heat Detectors | This recall involves mechanical heat detectors used indoors to detect elevated temperatures as part of professionally installed fire detection systems for residential homes and businesses. In residential settings, this product is installed in kitchens, attics and garages for property protection. The recalled heat detectors do not detect smoke or make an audible sound, but rather act as sensors that trigger fire alarms or security panels when elevated heat is detected. The heat detectors can be mounted to walls or ceilings and are labeled with “135F” and “NOT A LIFE SAFETY DEVICE.” The recalled units are the following: Model # Description Seller 281B-PL Heat Detector, 135F, Rate of Rise and Fixed Temperature Edwards 283B-PL Heat Detector, 135F, Fixed Temperature Edwards 104-13 Heat Detector, 135F, Rate of Rise and Fixed temperature Interlogix 104-15 Heat Detector, 135F, Fixed Temperature Interlogix 1EYC2 Heat Detector, 135F, Rate of Rise and Fixed Temperature Edwards, Grainger P/N 1EYC4 Heat Detector, 135F, Fixed Temperature Edwards, Grainger P/N 281B-20pkg-OEM-UTCO1 Heat Detector, 135F, Rate of Rise and Fixed Temperature Honeywell Security 281B-20pkg-OEM-UTC20 Heat Detector, 135F, Rate of Rise and Fixed Temperature Interlogix 281B-OEM-UTC01 Heat Detector, 135F, Rate of Rise and Fixed Temperature Honeywell Security 283B-20pkg-OEM-UTC01 Heat Detector, 135F, Fixed Temperature Honeywell Security 73340U Heat Detector, 135F, Fixed Temperature and Rate of Rise Mirtone 73342U Heat Detector, 135F, Fixed Temperature Mirtone AI281B Heat Detector, 135F, Fixed Temperature and Rate of Rise Edwards AI283B Heat Detector, 135F, Fixed Temperature Edwards 281A Heat Detector, 135F, Fixed Temperature and Rate of Rise Edwards | The recalled heat detectors can fail to activate in reaction to rising temperatures, posing a risk of failure to alert consumers to a fire. | Replace | About 85,000 | None reported | Consumers who use the product in life-safety applications permitted by code (for example, in elevator shafts, or in lieu of smoke detectors, manual pull stations, or sprinklers in particular settings), or in residential attics or residential garages, should immediately contact a fire or security alarm professional for free replacement and installation of the heat detector. | Sold At | Edwards’ distributors, electrical wholesalers, contractors, and fire safety professionals nationwide from January 1979 through May 2018 for between $6 to $7 per unit. | Edwards Fire Safety, of Bradenton, Florida |  |  | China
19-162 | July 10, 2019 | Universal Security Instruments Recalls to Inspect Smoke Alarms Due to Risk of Failure to Alert Consumers to a Fire | Battery powered smoke and fire alarms | This recall involves Universal Security Instruments 10 year battery-operated ionization smoke and fire alarms with model numbers MI3050S and MI3050SB and with date codes between 2015JAN19 through 2016JUL11. The smoke alarms are white in color and 5½&nbsp; inches in diameter.&nbsp; “Universal” and “Smoke &amp; Fire Alarm” are printed on the front cover of the alarm. The label on the back of the alarm lists the model number and date code.&nbsp; | The smoke alarms can have a misaligned internal switch causing the alarms to not activate properly, posing a risk of failure to alert consumers to a fire. | Replace | About 180,000 | The company has received 134 reports of failure to properly activate during installation. | Consumers should immediately inspect their smoke alarms to determine if it will activate appropriately. Press the test button to determine if it is operating properly. If the alarm sounds no further action is required. Additional instructions are located on the firm’s website. If smoke alarm does not sound during the test, consumers should immediately contact Universal Security for a replacement. | Sold At | Online through specialty wholesalers and others from July 2015 to December 2016 about $20 | Universal Security Instruments, of Owings Mills, Md. |  |  | Hong Kong
19-141 | June 21, 2019 | Honeywell Recalls Gamewell-FCI and Notifier Photoelectric Smoke Sensors Sold with Fire Alarm Systems Due to Failure to Alert of a Fire | “-IV” Intelligent photoelectric smoke sensors sold with fire alarm systems | This recall involves “-IV” Intelligent photoelectric smoke sensors sold with fire alarm systems installed primarily in commercial buildings; not sold to retailers or consumers. The smoke sensors are round, ivory in color, and measure four inches in diameter. The model number, date codes and Honeywell or Notifier are printed on the back label of the smoke sensor. The smoke sensors have the following brand names, model numbers, date codes, and configuration. &nbsp; &nbsp; &nbsp; Brand Model Date code range Operating mode Connected to Panels Gamewell-FCI ASD-PL3-IV 8034 to 9013 CLIP S3 series and E3 series &nbsp; ASD-PL3R-IV &nbsp; &nbsp; &nbsp; &nbsp; ASD-PTL3-IV &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; Notifier FSP-951-IV &nbsp; &nbsp; NFS-3030 and NFS2-3030 &nbsp; FSP-951R-IV &nbsp; &nbsp; &nbsp; &nbsp; FSP-951T-IV &nbsp; &nbsp; &nbsp; | The photoelectric smoke sensor can malfunction and cause the fire alarm system to fail to alert occupants in commercial buildings of a fire. | Replace | About 22,000 | None reported | Consumers should immediately contact Gamewell-FCI or Notifier to receive a free replacement photoelectric smoke sensor. | Sold At | Gamewell-FCI and Notifier distributors nationwide between March 2018 and January 2019 for about $115. |  | Honeywell International Inc., of Northford, Conn. |  | Mexico
18-128 | March 21, 2018 | Kidde Recalls Dual Sensor Smoke Alarms Due to Risk of Failure to Alert Consumers to a Fire | Kidde dual-sensor (photoelectric and ionization) smoke alarms – models PI2010 and PI9010 |  | A yellow cap left on during the manufacturing process can cover one of the two smoke sensors and compromise the smoke alarm’s ability to detect smoke, posing a risk of consumers not being alerted to a fire in their home. | Replace | About 452,000 in the U.S. (In addition, about 40,000 were sold in Canada.) | The firm has received one report of the yellow protective cap being present on a smoke alarm before it was installed in a consumer’s home. No reports of incidents or injuries as a result of a yellow cap being present have been reported. | Consumers should remove the alarm from the wall/ceiling and visually inspect it through the opening on the side of the alarm for the presence of a yellow cap. Consumers should not attempt to take apart the alarm, open the casing, or otherwise remove the yellow cap themselves. If a yellow cap is present, the consumer should immediately contact Kidde to receive instructions and request a free replacement smoke alarm. They should remove and discard the recalled smoke alarm only after they receive and install the replacement alarm. If no yellow cap is present, consumers should reinstall the smoke alarm and no further action is needed. | Sold At | Menards, The Home Depot, Walmart and other department, home and hardware stores nationwide and online at Amazon.com, ShopKidde.com and other websites from September 2016 through January 2018 for between $20 and $40. | Walter Kidde Portable Equipment Company Inc., of Mebane, N.C. | Fyrnetics Limited, of Hong Kong | Walter Kidde Portable Equipment Company Inc., of Mebane, N.C. | China
17-151 | May 12, 2017 | Honeywell International Recalls SWIFT® Wireless Gateway Sold with Fire Alarm Systems Due To Failure to Communicate in Fire | SWIFT wireless gateway sold with fire alarm systems | This recall involves the SWIFT wireless gateway sold with fire alarm systems. The gateways are round, white and measure eight inches in diameter. The gateways are the bridge between the fire alarm control panel and the detectors. These systems are used primarily for indoor or covered areas in commercial buildings, such as in office buildings, hotels, industrial facilities, and apartment complexes. The model number and date codes are printed on the back of the gateway on a white label on the circuit board. The gateways have the following brand names, model numbers and date codes. &nbsp; &nbsp; Brand Model Date Code Range NOTIFIER FWSG &nbsp; 10 13 14 through 12 15 16 &nbsp; &nbsp; Fire-Lite W-GATE Gamewell-FCI VW-GATE Honeywell XLS-WSG Johnson Controls JFWSG &nbsp; | The smoke detectors connected to the gateway can fail to activate properly when significant environmental contaminants are present, posing a risk that consumers will not be alerted to a fire. | Repair | About 900 | None reported | Contact Honeywell for an update of the firmware on the SWIFT wireless gateway(s) installed on the system. Commercial building customers should continue using the recalled detectors until the firmware is updated. | Sold At | Honeywell distributors nationwide between October 2014 and December 2016 for about $440 for the fire alarm system. |  | Honeywell International Inc., of Northford, Conn. |  | United States
17-031 | November 10, 2016 | Kidde Recalls Combination Smoke/CO Alarms Due to Alarm Failure | Combination smoke/carbon monoxide (CO) alarms | This recall involves Kidde NightHawk talking combo smoke/CO alarm with model number KN-COSM-IB and manufacture dates between June 1, 2004 and December 31, 2010. The alarms are hard-wired into a home’s electric power.&nbsp;The unit has a compartment on the back for the installation of a replaceable 9V backup battery. The alarm is white, round and measures about 5 to 6 inches in diameter.&nbsp;“Kidde” is engraved on the front of the alarm. “Kidde,” the model number and manufacture dates are printed on a label on the back on the alarm. | The combination smoke/carbon monoxide (CO) alarm can fail to continue to chirp when it reaches its 7-year end of life if the batteries are replaced, leading consumers to believe it is still working. This poses a risk of consumers not being alerted to a fire or CO incident in their home. | Replace | About 3.6 million (in addition 1.5 million were sold in Canada) | Kidde has received eight reports of incidents with the recalled alarms. No injuries have been reported. | Consumers should immediately stop using the recalled alarms and contact Kidde directly for a free replacement alarm based on date of manufacture or a discount on a new alarm. | Sold At | Electrical distributors and home centers nationwide and online at Amazon.com from June 2004 through December 2010 for between $40 and $65. | Walter Kidde Portable Equipment Inc., of Mebane, N.C. |  |  | China
16-039 | November 18, 2015 | Recalled Products Sold by Home Depot After Recalls Were Announced | 28 different recalled products | Hazards include fire, burn, shock, falls, lacerations or other injuries depending on the product. | Hazards include fire, burn, shock, falls, lacerations or other injuries depending on the product. | Repair, Refund, Replace
16-021 | October 29, 2015 | Sure Signal Products Recalls Heat-Activated Fire Alarms Due to Failure to Alert Consumers of a Fire | Heat-activated fire alarm | A defective fuse on DeTech, MasterGuard, Responsive and Thermalink fire alarms can cause the alarm to fail to signal an alert. | A defective fusible link sensor (fuse) on the fire alarm can cause the alarm to fail to alert consumers of a fire. | Replace | About 375,000 | None reported | Consumers should immediately contact Sure Signal Products for free replacement fuses. A video with instructions on how to replace the fuse is available at http://SureSignalProducts.com. | Sold At | Fire alarm dealers nationwide from January 2004 through September 2015 for between $300 and $375. | Sure Signal Products, Inc., de Garden Grove, California | Sure Signal Products, Inc., of Garden Grove, Calif. |  | United States
15-753 | September 09, 2015 | Bosch Security Systems Recalls Wireless Smoke Alarms Due to Failure to Alert Consumers to a Fire (Recall Alert) | Radion wireless smoke alarms | The alarms can fail to alert consumers to a fire, posing a fire hazard. | The alarms can fail to alert consumers to a fire, posing a fire hazard. | Replace | About 950 | Bosch has received two reports that alarms failed to sound during installation testing. | Consumers should immediately contact their dealer/installer for a free replacement alarm. Bosch has contacted dealers and installers directly. | Sold At | Security system dealers nationwide from November 2013 through October 2014 for about $125. |  | Bosch Security Systems Inc., Fairport, N.Y. |  | China
14-278 | September 18, 2014 | Siemens Recalls Audible Fire Alarm Base Due to Risk of Injury | SBGA-34 Audible Fire Alarm Base | The Siemens SBGA-34 audible fire alarm base can fail to sound an alarm, posing a risk of personal injury and property damage. | The fire alarm base can fail to sound an alarm, posing a risk of personal injury and property damage. | Replace | About 9,000 | None reported. | Consumers should immediately contact Siemens to schedule a free inspection and replacement of the recalled audible base. | Sold At | Siemens sales offices, authorized distributors and installers nationwide from February 2013 through June 2014 for about $120. |  |  |  | China
14-275 | September 11, 2014 | Kidde Recalls Smoke and Combination Smoke/CO Alarms Due to Alarm Failure | Kidde hard-wired smoke and combination smoke/carbon monoxide (CO) alarms | The alarms could fail to alert consumers of a fire or CO incident after a power outage. | The alarms could fail to alert consumers of a fire or a CO incident following a power outage. | Replace | About 1.2 million in the United States and about 112,000 in Canada | None reported | Consumers should immediately contact Kidde for a free replacement smoke or combination smoke/CO alarm. Consumers should keep using the recalled alarms until they install replacement alarms. | Sold At | CED, City Electric Supply, HD Supply, Home Depot, Menards Inc. and other retailers, electrical distributors and online at Amazon.com, HomeDepot.com and shopkidde.com from January 2014 through July 2014 for between $30 and $50. |  |  |  | China
14-255 | August 13, 2014 | ESL, Interlogix Hard-Wired Smoke Alarms Recalled Due to Failure to Alert Consumers of a Fire | ESL and Interlogix brand 400/500 series smoke detectors | Radio frequency interference can cause the smoke detectors to fail. | Radio frequency interference can cause the smoke detectors to fail to alert consumers of a fire. | Replace | About 141,000 in U.S. and 13,000 in Canada | None. | Customers should immediately contact their security or fire system provider to determine if any of their units are included in the recall. If so, they will receive free replacement and free installation of new smoke detectors. Consumers should not take the alarms out of service until the replacement alarm has been installed. Only professional installers should remove and replace these units. | Sold At | Alarm system, security equipment and electrical equipment contractors, dealers and installers for use in fire alarm systems for commercial buildings, hotels/motels, apartments, dormitories and homes from March 2013 to February 2014. The cost of the individual detectors varies between $30 and $50. The cost of the integrated alarm or security systems varies greatly. |  |  |  | China
14-187 | May 21, 2014 | Nest Labs Recalls to Repair Nest Protect Smoke + CO Alarms Due to Failure to Sound Alert | Nest Protect: Smoke + CO Alarm | Activity near the alarm during a fire can prevent the alarm from immediately sounding when the Nest Wave feature is turned on. | Activity near the product during a fire can prevent the alarm from immediately sounding when the Nest Wave feature is enabled. | Repair, Refund | About 440,000 | Nest Labs has received no reports of incidents, injuries or property damage. | The repair is an automatic electronic update that disables the Nest Wave feature and is delivered automatically to devices connected wirelessly to the Internet and linked to a Nest account. Consumers should take one of the following actions: Consumers who have not connected their Nest Protect devices to their wireless network and linked them to a Nest account should immediately do so. The devices will automatically receive the update that disables the Nest Wave feature. Customers should confirm that their devices have been updated by going to Nest Sense on their Nest account mobile or web application and ensuring that the button for Nest Wave is off and grayed out. Instructions on how to connect to a network and disable the feature are available at http://support.nest.com/article/Nest-Protect-Safety or by contacting Nest Labs. Consumers whose Nest Protect devices are connected to their wireless network and linked to a Nest account should immediately confirm the receipt of an automatic repair that disabled the Nest Wave feature by going to Nest Sense on their Nest account mobile or web application and ensuring that the button for Nest Wave is set to "off" and grayed out. No further action is required and consumers can continue to use their devices. | Sold At | Best Buy, Home Depot and other retailers nationwide, and online at nest.com, amazon.com, bestbuy.com and homedepot.com from November 15, 2013 to April 3, 2014 for about $130. |  |  |  | China.
14-713 | January 28, 2014 | System Sensor Recalls Reflected Beam Smoke Detectors Due To Failure to Alert Consumers in a Fire (Recall Alert) | System Sensor reflected beam smoke detectors | This recall involves System Sensor's reflected beam smoke detectors with model number BEAM1224S and date codes 2111 through 3053. The YMMW format date codes stand for (2111) 2012-November-1st week of Nov. through (3053) 2013-May-3rd week of May. The detectors are ivory and black and measure 10 inches high by 7? inches wide. The model number and date code are printed on a label on the back of the detector's cover and on the product's packaging. The reflected beam smoke detectors were used primarily in commercial buildings as part of the fire alarm system. Detectors used with acceptable power supplies, as listed on the company website, do not need to be replaced. | When used with certain power supplies, the reflected beam smoke detectors can fail to send a signal to the fire alarm control panel that sounds the alarm and fail to alert occupants of a fire. | Replace | About 610 | None reported | Owners with the affected smoke detectors powered by a power supply that is not on the company's acceptable list available online, should contact System Sensor to receive free replacement smoke detectors. System Sensor and its distributors are contacting purchasers directly. | Sold At | Alarm system, security equipment and electrical equipment contractors and dealers for use in commercial building fire alarm systems from November 2012 through May 2013 for about $800. |  |  |  | United States
11300 | August 08, 2011 | Emergency Exit Signs Recalled by Best Lighting Products Due to Failure to Illuminate | LHQM LED Exit Signs with Emergency Lights | The U.S. Consumer Product Safety Commission, in cooperation with the firm named below, today announced a voluntary recall of the following consumer product. Consumers should stop using recalled products immediately unless otherwise instructed. It is illegal to resell or attempt to resell a recalled consumer product. | The fixtures can malfunction and fail to illuminate in the event of a power failure. This could result in a failure to provide adequate lighting to guide building occupants to an exit in the event of an emergency. | Replace | About 450 | There were ten reports of signs malfunctioning during testing after installation. No injuries were reported. | Consumers should contact Lithonia Lighting for a free replacement product. | Sold At | Authorized distributors nationwide from January 2011 through May 2011 for $100 to $200. |  | Best Lighting Products, of Pataskala, Ohio | Lithonia Lighting, a division of Acuity Brands Lighting Inc. of Conyers, Ga. | China
11-721 | February 07, 2011 | Simplex Fire Alarm Control Panels Recalled by Tyco Safety Products Westminster Due to Failure to Alert Monitoring Centers |  | The recalled fire alarm control panels can fail to send a signal to alert monitoring centers in the event of a fire. | The recalled fire alarm control panels can fail to send a signal to alert monitoring centers in the event of a fire. | New Instructions | About 540 | The firm has received 2 reports of alarms failing to alert monitoring centers. No injuries have been reported. | Building managers should contact SimplexGrinnell for a free software upgrade. SimplexGrinnell is contacting its customers directly. | Sold At | "Distributed by SimplexGrinnell from May 2010 to September 2010 for between $10,000 and $20,000." |  | "Tyco Safety Products Westminster of Westminster, Mass." |  | U.S.
11702 | October 04, 2010 | Fire Alarm Control Panels Recalled by Fire-Lite Alarms Due to Alert Failure | Fire Alarm Control Panel | The following product safety recall was voluntarily conducted by the firm in cooperation with the CPSC. Building managers should stop relying on this product's models listed below to provide adequate fire warning. It is illegal to resell or attempt to resell a recalled consumer product. | The recalled fire alarm control panels used with an SLC-2LS expander module can fail to sound an alarm in the event of a fire. | New Instructions | About 530 | None reported. | Building managers should contact Fire-Lite Alarms for a free software upgrade. Fire-Lite Alarms is contacting its customers directly. | Sold At | Authorized wholesalers and distributors nationwide from October 2008 through March 2010 for between about $875 for the expander module and $2,285 for the control panel. These distributors resold and/or installed the control panels and modules for use in commercial facilities such as office buildings. |  | Fire-Lite Alarms of Northford, Conn. |  | United States
09-266 | July 08, 2009 | Kidde Recalls Dual Sensor Smoke Alarms; Can Fail to Warn of a Fire
09-717 | December 29, 2008 | Fire Alarm Control Panels Recalled by Notifier Due to Alert Failure
08-267 | May 14, 2008 | Maple Chase Co. Recalls Carbon Monoxide and Carbon Monoxide/Smoke Combo Alarms Due to Alarm Malfunction
07-575 | September 05, 2007 | Apex Security Systems with XICOR Memory Chip Recalled by Honeywell International; Could Fail to Warn of Fire, Intrusion
07-565 | July 26, 2007 | Gamewell-FCI Recalls to Upgrade Software Used with Fire Alarm System Control Panels
07-136 | March 21, 2007 | Digital Security Controls Recalls Smoke Detectors that Could Fail to Warn of a Fire
07-526 | January 30, 2007 | Gamewell-FCI Recalls to Upgrade Software Used with Fire Alarm System Control Boards
06-551 | May 18, 2006 | Tyco Fire & Security Announces Recall to Upgrade Software of Fire Detection Systems
06-550 | May 18, 2006 | Tyco Fire & Security Recalls Smoke Detectors for Replacement
06-151 | May 01, 2006 | First Alert&#174; Smoke Alarms and Combination Smoke/CO Alarms Recalled for Rapidly Draining Battery Power
05-548 | March 07, 2005 | CPSC, Honeywell Sensing and Controls Announce Recall of Thermal Switches
05-526 | December 21, 2004 | CPSC, GE Security Inc. Announce Retrofit/Recall of Smoke Detector Systems
04-508 | October 29, 2003 | CPSC, Notifier Announce Recall for Fire Alarm Panels
04-507 | October 29, 2003 | CPSC, Fire Control Instruments Announce Recall for Audio Evacuation Units
03-552 | September 02, 2003 | CPSC, GE Interlogix Announce Recall of Smoke Detectors
03-527 | March 10, 2003 | CPSC, Fire-Lite Alarms Announce Recall of Power Supply for Alarm Systems
00-115 | May 24, 2000 | CPSC, Universal Security Instruments Announce Recall of Smoke Alarms